## T13
tag | type | Element_Name | Measured_Variable | address | Installed Power | Category | tag | SDG_ODBC | T13 ((Measured Value), short floating point number)
1 | T13 | PV1 | F | 16442 | 999 | A | TAGW0 | TAGW1 | PV1 ¦ Inverter - Grid Frequency
2 | T13 | PV1 | Ib | 16437 | 999 | A | TAGW2 | TAGW2 | PV1 ¦ Inverter - Phase B Current
3 | T13 | PV1 | Vb | 16434 | 999 | A | TAGW4 | TAGW3 | PV1 ¦ Inverter - Phase B Voltage
4 | T13 | PV1 | Prt | 16401 | 999 | A | TAGW6 | TAGW4 | PV1 ¦ Subarray Inverter - Real-time Active Power
5 | T13 | PV1 | Qrt | 16403 | 999 | A | TAGW8 | TAGW5 | PV1 ¦ Subarray Inverter - Real-time Reactive Power
6 | T13 | PV1 | Pfv | 16418 | 999 | A | TAGW10 | TAGW6 | PV1 ¦ Subarray Inverter - Active Power (Feedback Value)
7 | T13 | PV1 | PRfv | 16419 | 999 | A | TAGW12 | TAGW7 | PV1 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
8 | T13 | PV1 | PF | 16420 | 999 | A | TAGW14 | TAGW8 | PV1 ¦ Subarray Inverter - Power Factor (Feedback Value)
9 | T13 | PV1 | Qfv | 16421 | 999 | A | TAGW16 | TAGW9 | PV1 ¦ Subarray Inverter - Reactive Power (Feedback Value)
10 | T13 | PV1 | QRfv | 16423 | 999 | A | TAGW18 | TAGW10 | PV1 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
11 | T13 | PV2 | F | 16442 | 999 | A | TAGW20 | TAGW11 | PV2 ¦ Inverter - Grid Frequency
12 | T13 | PV2 | Ib | 16437 | 999 | A | TAGW22 | TAGW12 | PV2 ¦ Inverter - Phase B Current
13 | T13 | PV2 | Vb | 16434 | 999 | A | TAGW24 | TAGW13 | PV2 ¦ Inverter - Phase B Voltage
14 | T13 | PV2 | Prt | 16401 | 999 | A | TAGW26 | TAGW14 | PV2 ¦ Subarray Inverter - Real-time Active Power
15 | T13 | PV2 | Qrt | 16403 | 999 | A | TAGW28 | TAGW15 | PV2 ¦ Subarray Inverter - Real-time Reactive Power
16 | T13 | PV2 | Pfv | 16418 | 999 | A | TAGW30 | TAGW16 | PV2 ¦ Subarray Inverter - Active Power (Feedback Value)
17 | T13 | PV2 | PRfv | 16419 | 999 | A | TAGW32 | TAGW17 | PV2 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
18 | T13 | PV2 | PF | 16420 | 999 | A | TAGW34 | TAGW18 | PV2 ¦ Subarray Inverter - Power Factor (Feedback Value)
19 | T13 | PV2 | Qfv | 16421 | 999 | A | TAGW36 | TAGW19 | PV2 ¦ Subarray Inverter - Reactive Power (Feedback Value)
20 | T13 | PV2 | QRfv | 16423 | 999 | A | TAGW38 | TAGW20 | PV2 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
21 | T13 | PV3 | F | 16442 | 359.34 | A | TAGW40 | TAGW21 | PV3 ¦ Inverter - Grid Frequency
22 | T13 | PV3 | Ib | 16437 | 359.34 | A | TAGW42 | TAGW22 | PV3 ¦ Inverter - Phase B Current
23 | T13 | PV3 | Vb | 16434 | 359.34 | A | TAGW44 | TAGW23 | PV3 ¦ Inverter - Phase B Voltage
24 | T13 | PV3 | Prt | 16401 | 359.34 | A | TAGW46 | TAGW24 | PV3 ¦ Subarray Inverter - Real-time Active Power
25 | T13 | PV3 | Qrt | 16403 | 359.34 | A | TAGW48 | TAGW25 | PV3 ¦ Subarray Inverter - Real-time Reactive Power
26 | T13 | PV3 | Pfv | 16418 | 359.34 | A | TAGW50 | TAGW26 | PV3 ¦ Subarray Inverter - Active Power (Feedback Value)
27 | T13 | PV3 | PRfv | 16419 | 359.34 | A | TAGW52 | TAGW27 | PV3 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
28 | T13 | PV3 | PF | 16420 | 359.34 | A | TAGW54 | TAGW28 | PV3 ¦ Subarray Inverter - Power Factor (Feedback Value)
29 | T13 | PV3 | Qfv | 16421 | 359.34 | A | TAGW56 | TAGW29 | PV3 ¦ Subarray Inverter - Reactive Power (Feedback Value)
30 | T13 | PV3 | QRfv | 16423 | 359.34 | A | TAGW58 | TAGW30 | PV3 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
31 | T13 | PV4 | F | 16442 | 999.5 | A | TAGW60 | TAGW31 | PV4 ¦ Inverter - Grid Frequency
32 | T13 | PV4 | Ib | 16437 | 999.5 | A | TAGW62 | TAGW32 | PV4 ¦ Inverter - Phase B Current
33 | T13 | PV4 | Vb | 16434 | 999.5 | A | TAGW64 | TAGW33 | PV4 ¦ Inverter - Phase B Voltage
34 | T13 | PV4 | Prt | 16401 | 999.5 | A | TAGW66 | TAGW34 | PV4 ¦ Subarray Inverter - Real-time Active Power
35 | T13 | PV4 | Qrt | 16403 | 999.5 | A | TAGW68 | TAGW35 | PV4 ¦ Subarray Inverter - Real-time Reactive Power
36 | T13 | PV4 | Pfv | 16418 | 999.5 | A | TAGW70 | TAGW36 | PV4 ¦ Subarray Inverter - Active Power (Feedback Value)
37 | T13 | PV4 | PRfv | 16419 | 999.5 | A | TAGW72 | TAGW37 | PV4 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
38 | T13 | PV4 | PF | 16420 | 999.5 | A | TAGW74 | TAGW38 | PV4 ¦ Subarray Inverter - Power Factor (Feedback Value)
39 | T13 | PV4 | Qfv | 16421 | 999.5 | A | TAGW76 | TAGW39 | PV4 ¦ Subarray Inverter - Reactive Power (Feedback Value)
40 | T13 | PV4 | QRfv | 16423 | 999.5 | A | TAGW78 | TAGW40 | PV4 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
41 | T13 | PV5 | F | 16442 | 399.52 | A | TAGW80 | TAGW41 | PV5 ¦ Inverter - Grid Frequency
42 | T13 | PV5 | Ib | 16437 | 399.52 | A | TAGW82 | TAGW42 | PV5 ¦ Inverter - Phase B Current
43 | T13 | PV5 | Vb | 16434 | 399.52 | A | TAGW84 | TAGW43 | PV5 ¦ Inverter - Phase B Voltage
44 | T13 | PV5 | Prt | 16401 | 399.52 | A | TAGW86 | TAGW44 | PV5 ¦ Subarray Inverter - Real-time Active Power
45 | T13 | PV5 | Qrt | 16403 | 399.52 | A | TAGW88 | TAGW45 | PV5 ¦ Subarray Inverter - Real-time Reactive Power
46 | T13 | PV5 | Pfv | 16418 | 399.52 | A | TAGW90 | TAGW46 | PV5 ¦ Subarray Inverter - Active Power (Feedback Value)
47 | T13 | PV5 | PRfv | 16419 | 399.52 | A | TAGW92 | TAGW47 | PV5 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
48 | T13 | PV5 | PF | 16420 | 399.52 | A | TAGW94 | TAGW48 | PV5 ¦ Subarray Inverter - Power Factor (Feedback Value)
49 | T13 | PV5 | Qfv | 16421 | 399.52 | A | TAGW96 | TAGW49 | PV5 ¦ Subarray Inverter - Reactive Power (Feedback Value)
50 | T13 | PV5 | QRfv | 16423 | 399.52 | A | TAGW98 | TAGW50 | PV5 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
51 | T13 | PV6 | F | 16442 | 499.32 | A | TAGW100 | TAGW51 | PV6 ¦ Inverter - Grid Frequency
52 | T13 | PV6 | Ib | 16437 | 499.32 | A | TAGW102 | TAGW52 | PV6 ¦ Inverter - Phase B Current
53 | T13 | PV6 | Vb | 16434 | 499.32 | A | TAGW104 | TAGW53 | PV6 ¦ Inverter - Phase B Voltage
54 | T13 | PV6 | Prt | 16401 | 499.32 | A | TAGW106 | TAGW54 | PV6 ¦ Subarray Inverter - Real-time Active Power
55 | T13 | PV6 | Qrt | 16403 | 499.32 | A | TAGW108 | TAGW55 | PV6 ¦ Subarray Inverter - Real-time Reactive Power
56 | T13 | PV6 | Pfv | 16418 | 499.32 | A | TAGW110 | TAGW56 | PV6 ¦ Subarray Inverter - Active Power (Feedback Value)
57 | T13 | PV6 | PRfv | 16419 | 499.32 | A | TAGW112 | TAGW57 | PV6 ¦ Subarray Inverter - Active Power Ratio (Feedback Value)
58 | T13 | PV6 | PF | 16420 | 499.32 | A | TAGW114 | TAGW58 | PV6 ¦ Subarray Inverter - Power Factor (Feedback Value)
59 | T13 | PV6 | Qfv | 16421 | 499.32 | A | TAGW116 | TAGW59 | PV6 ¦ Subarray Inverter - Reactive Power (Feedback Value)
60 | T13 | PV6 | QRfv | 16423 | 499.32 | A | TAGW118 | TAGW60 | PV6 ¦ Subarray Inverter - Reactive Power Ratio (Feedback Value)
61 | T13 | TRIAD | I1 |  |  |  |  | TAGW61 | TRIAD I1
62 | T13 | TRIAD | I2 |  |  |  |  | TAGW62 | TRIAD I2
63 | T13 | TRIAD | I3 |  |  |  |  | TAGW63 | TRIAD I3
64 | T13 | TRIAD | V12 |  |  |  |  | TAGW64 | TRIAD V12
65 | T13 | TRIAD | V23 |  |  |  |  | TAGW65 | TRIAD V23
66 | T13 | TRIAD | V31 |  |  |  |  | TAGW66 | TRIAD V31
67 | T13 | TRIAD | PTOT |  |  |  |  | TAGW67 | TRIAD PTOT
68 | T13 | TRIAD | QTOT |  |  |  |  | TAGW68 | TRIAD QTOT

## T50
tag | Element_Name | type | Set-point type | T50 (set point command, short floating point number) | address | SDG_ODBC
1 | PV1 | T50 | Pst | PV1 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR1
2 | PV1 | T50 | Pr | PV1 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR2
3 | PV1 | T50 | PFst | PV1 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR3
4 | PV1 | T50 | Qst | PV1 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR4
5 | PV1 | T50 | Qr | PV1 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR5
6 | PV2 | T50 | Pst | PV2 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR6
7 | PV2 | T50 | Pr | PV2 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR7
8 | PV2 | T50 | PFst | PV2 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR8
9 | PV2 | T50 | Qst | PV2 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR9
10 | PV2 | T50 | Qr | PV2 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR10
11 | PV3 | T50 | Pst | PV3 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR11
12 | PV3 | T50 | Pr | PV3 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR12
13 | PV3 | T50 | PFst | PV3 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR13
14 | PV3 | T50 | Qst | PV3 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR14
15 | PV3 | T50 | Qr | PV3 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR15
16 | PV4 | T50 | Pst | PV4 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR16
17 | PV4 | T50 | Pr | PV4 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR17
18 | PV4 | T50 | PFst | PV4 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR18
19 | PV4 | T50 | Qst | PV4 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR19
20 | PV4 | T50 | Qr | PV4 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR20
21 | PV5 | T50 | Pst | PV5 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR21
22 | PV5 | T50 | Pr | PV5 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR22
23 | PV5 | T50 | PFst | PV5 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR23
24 | PV5 | T50 | Qst | PV5 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR24
25 | PV5 | T50 | Qr | PV5 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR25
26 | PV6 | T50 | Pst | PV6 ¦ Subarray inverter - Setpoint Command for Active Power | 25089 | TAGR26
27 | PV6 | T50 | Pr | PV6 ¦ Subarray inverter - Setpoint Command for Active Power Ratio | 25090 | TAGR27
28 | PV6 | T50 | PFst | PV6 ¦ Subarray inverter - Setpoint Command for Power Factor | 25091 | TAGR28
29 | PV6 | T50 | Qst | PV6 ¦ Subarray inverter - Setpoint Command for Reactive Power | 25092 | TAGR29
30 | PV6 | T50 | Qr | PV6 ¦ Subarray inverter - Setpoint Command for Reactive Power Ratio | 25093 | TAGR30