## bus
| name | vn_kv | type | zone | in_service | description | substat | folder_id | sernum | for_name | chr_name
0 | 0 / 150 kV BB | 150 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
1 | 1 / Substation 2 | 20 | m | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
2 | 10 / PAN-0060Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
3 | 11 / LV 116310 | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
4 | 12 / 588 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
5 | 13 / MV PASA NERO | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
6 | 14 / LV PASA NERO | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
7 | 15 / PAN-0058Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
8 | 16 / LV ARSENA AMPELIA | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
9 | 17 / 518 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
10 | 18 / PAN-0062Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
11 | 19 / LV 114875 | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
12 | 2 / 866 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
13 | 20 / Μ-624 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
14 | 21 / 438 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
15 | 22 / PAN-0064Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
16 | 23 / LV VASILINO | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
17 | 24 / PAN-0063Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
18 | 25 / LV GIOUNA LAKKA | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
19 | 26 / 164 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
20 | 27 / PAN-0065X | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
21 | 3 / MV 116308 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
22 | 4 / LV 116308 | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
23 | 5 / Μ-617 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
24 | 6 / 686 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
25 | 7 / PΑΝ-0059Χ | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
26 | 8 / LV VAFTSA | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
27 | 9 / 602 | 20 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA
28 | LV Aggregated | 0.4 | b | 32-STAGEIRA | TRUE | 32-STAGEIRA |  | 32-STAGEIRA

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | description | sernum | for_name | chr_name
0 | ARSENA AMPELIA-117613 | 8 | 0.9999 | -0.48427 | 0.9999 | 1 | TRUE | PV | TRUE
1 | Aggregated_PV | 28 | 5.363 | -2.5974 | 5.363 | 1 | TRUE | PV | TRUE
2 | GIOUNA LAKKA-117169 | 18 | 0.9999 | -0.48427 | 0.9999 | 1 | TRUE | PV | TRUE
3 | PASA NERO-116978 | 6 | 0.39996 | -0.19371 | 0.39996 | 1 | TRUE | PV | TRUE
4 | PV System | 22 | 0.8698 | -0.42126 | 0.8698 | 1 | TRUE | PV | TRUE
5 | PV System 114875 | 11 | 1 | -0.48432 | 1 | 1 | TRUE | PV | TRUE
6 | PV System 116310 | 3 | 1 | -0.48432 | 1 | 1 | TRUE | PV | TRUE
7 | VAFTSA-117634 | 26 | 0.3597 | -0.17421 | 0.3597 | 1 | TRUE | PV | TRUE
8 | VASILINO-117622 | 16 | 0.9999 | -0.48427 | 0.9999 | 1 | TRUE | PV | TRUE

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 7 | 3 | t | CB | TRUE | 15 / PAN-0058Χ\Cub_1\Switch | 0
1 | 20 | 7 | t | CB | TRUE | 27 / PAN-0065X\Cub_1\Switch | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max | r0x0_max | x0x_max | r0x0_min | x0x_min | description
0 | External Grid | 0 | 1 | 0 | 1 | TRUE | 1606.6 | 1473.7 | 0.2352 | 0.2527 | 0.2631 | 3.2383 | 0.2631 | 2.9584

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km | alpha | temperature_degree_celsius | description | line_idx | folder_id | section_idx
0 | 1-2 | Synthetic Line 1 | 1 | 12 | 1 | 2.8107 | 3.1164 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 0 | 32-STAGEIRA | 0
1 | 12-13 | Synthetic Line 4 | 4 | 5 | 1 | 0.12096 | 0.08337 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 1 | 32-STAGEIRA | 0
2 | 12-15 | 35ACSR | 4 | 7 | 0.114 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 2 | 32-STAGEIRA | 0
3 | 17-18 | 35ACSR | 9 | 10 | 0.087 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 3 | 32-STAGEIRA | 0
4 | 17-20 | Synthetic Line 5 | 9 | 13 | 1 | 0.1677 | 0.26052 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 4 | 32-STAGEIRA | 0
5 | 2-3 | 35ACSR | 12 | 21 | 0.183 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 5 | 32-STAGEIRA | 0
6 | 2-5 | Synthetic Line 2 | 12 | 23 | 1 | 0.83415 | 1.063 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 6 | 32-STAGEIRA | 0
7 | 20-21 | Synthetic Line 7 | 13 | 14 | 1 | 0.32313 | 0.22272 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 7 | 32-STAGEIRA | 0
8 | 20-26 | Synthetic Line 6 | 13 | 19 | 1 | 0.85183 | 1.3233 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 8 | 32-STAGEIRA | 0
9 | 21-22 | 35ACSR | 14 | 15 | 0.248 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 9 | 32-STAGEIRA | 0
10 | 21-24 | 35ACSR | 14 | 17 | 0.812 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 10 | 32-STAGEIRA | 0
11 | 26-27 | Synthetic Line 8 | 19 | 20 | 1 | 0.52312 | 0.58019 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 11 | 32-STAGEIRA | 0
12 | 5-17 | 95ACSR | 23 | 9 | 0.66 | 0.215 | 0.334 | 0 | 0 | 0.448 | 1 | 1 | ol | TRUE | 0.363 | 1.556 | 0 | 0.00403 | 80 |  | 12 | 32-STAGEIRA | 0
13 | 5-6 | Synthetic Line 3 | 23 | 24 | 1 | 0.33465 | 0.23066 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 13 | 32-STAGEIRA | 0
14 | 6-7 | 35ACSR | 24 | 25 | 0.016 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 14 | 32-STAGEIRA | 0
15 | 6-9 | 35ACSR | 24 | 27 | 0.448 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 15 | 32-STAGEIRA | 0
16 | 9-10 | 35ACSR | 27 | 2 | 1.636 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 16 | 32-STAGEIRA | 0
17 | 9-12 | 35ACSR | 27 | 4 | 0.7 | 0.576 | 0.397 | 0 | 0 | 0.224 | 1 | 1 | ol | TRUE | 0.724 | 1.595 | 0 | 0.00403 | 80 |  | 17 | 32-STAGEIRA | 0

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_set_vm_pu | description | equipment
0 | 0-1 | TR 20MVA3 | 0 | 1 | 20 | 150 | 20 | 15.77 | 0.14434 | 0.2598 | 0.1573 | 30 | hv | 0 | -9 | 6 | 1.25 | 0 | 0 | FALSE | 1 | 1 | TRUE | 21 | 5.3444 | 100 | 0 | 0.9 | 1
1 | 10-11 | 1 MVA 20/0.4 kV Dyn11 ASEA | 2 | 3 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
2 | 13-14 | 0.4 MVA 20/0.4 kV Dyn11 ASEA | 5 | 6 | 0.4 | 20 | 0.4 | 6 | 1.2 | 1.2 | 0.30001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 1.2 | 100 | 0 | 0.9 | 1
3 | 15-16 | 1 MVA 20/0.4 kV Dyn11 ASEA | 7 | 8 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
4 | 18-19 | 1 MVA 20/0.4 kV Dyn11 ASEA | 10 | 11 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
5 | 22-23 | 1 MVA 20/0.4 kV Dyn11 ASEA | 15 | 16 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
6 | 24-25 | 1 MVA 20/0.4 kV Dyn11 ASEA | 17 | 18 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
7 | 27-28 | 5 MVA 20/0.4 kV Dyn11 ASEA | 20 | 28 | 5 | 20 | 0.4 | 5.999 | 1.0931 | 0 | 0 | 330 | [6 empty] | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96296 | 100 | 0 | 0.9 | 1
8 | 3-4 | 1 MVA 20/0.4 kV Dyn11 ASEA | 21 | 22 | 1 | 20 | 0.4 | 6 | 0.96 | 2.3 | 0.23001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 0.96 | 100 | 0 | 0.9 | 1
9 | 7-8 | 0.4 MVA 20/0.4 kV Dyn11 ASEA | 25 | 26 | 0.4 | 20 | 0.4 | 6 | 1.2 | 1.2 | 0.30001 | 330 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE | 6 | 1.2 | 100 | 0 | 0.9 | 1

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | endtemp_degree | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
Synthetic Line 7 | 0 | 0.32313 | 0.22272 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
35ACSR | 0 | 0.576 | 0.397 | 0.224 | ol | 0 | 0.00403 | 80 | 0.724 | 1.595 | 0
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
95ACSR | 0 | 0.215 | 0.334 | 0.448 | ol | 0 | 0.00403 | 80 | 0.363 | 1.556 | 0
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
Synthetic Line 6 | 0 | 0.85183 | 1.3233 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
Synthetic Line 5 | 0 | 0.1677 | 0.26052 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
Synthetic Line 4 | 0 | 0.12096 | 0.08337 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
Synthetic Line 2 | 0 | 0.83415 | 1.063 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
Synthetic Line 8 | 0 | 0.52312 | 0.58019 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
Synthetic Line 3 | 0 | 0.33465 | 0.23066 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
Synthetic Line 1 | 0 | 2.8107 | 3.1164 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
5 MVA 20/0.4 kV Dyn11 ASEA | 0 | 0 | 1.0931 | 5 | 0.4 | 20 | 5.999 | 330 | Dyn11 | [7 empty] | 6 | 0.96296 | 100 | 0 | 0.9
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
TR 20MVA3 | 0.1573 | 0.2598 | 0.14434 | 20 | 20 | 150 | 15.77 | 30 | Dyn1 | hv | 0 | -9 | 6 | 0 | 1.25 | FALSE | 21 | 5.3444 | 100 | 0 | 0.9
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
1 MVA 20/0.4 kV Dyn11 ASEA | 0.23001 | 2.3 | 0.96 | 1 | 0.4 | 20 | 6 | 330 | Dyn11 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE | 6 | 0.96 | 100 | 0 | 0.9
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.4 MVA 20/0.4 kV Dyn11 ASEA | 0.30001 | 1.2 | 1.2 | 0.4 | 0.4 | 20 | 6 | 330 | Dyn11 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE | 6 | 1.2 | 100 | 0 | 0.9

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar | pf_vm_pu | pf_va_degree
0 |  |  |  |  | 1 | 0
1 |  |  |  |  | 0.91613 | -25.2021
2 |  |  |  |  | 0.93038 | -12.2286
3 |  |  |  |  | 0.90658 | 22.1111
4 |  |  |  |  | 0.92978 | -12.307
5 |  |  |  |  | 0.92986 | -12.297
6 |  |  |  |  | 0.90892 | 22.0816
7 |  |  |  |  | 0.92989 | -12.2934
8 |  |  |  |  | 0.90608 | 22.0506
9 |  |  |  |  | 0.9265 | -12.3289
10 |  |  |  |  | 0.92658 | -12.3185
11 |  |  |  |  | 0.90266 | 22.0581
12 |  |  |  |  | 0.92292 | -15.5906
13 |  |  |  |  | 0.92654 | -11.8962
14 |  |  |  |  | 0.92756 | -11.7614
15 |  |  |  |  | 0.92778 | -11.7317
16 |  |  |  |  | 0.9039 | 22.6327
17 |  |  |  |  | 0.9283 | -11.664
18 |  |  |  |  | 0.90443 | 22.6953
19 |  |  |  |  | 0.92683 | -10.295
20 |  |  |  |  | 0.92931 | -9.5162
21 |  |  |  |  | 0.92307 | -15.5715
22 |  |  |  |  | 0.90255 | 18.2488
23 |  |  |  |  | 0.92648 | -12.7449
24 |  |  |  |  | 0.92792 | -12.5527
25 |  |  |  |  | 0.92793 | -12.552
26 |  |  |  |  | 0.90934 | 21.391
27 |  |  |  |  | 0.92889 | -12.424
28 |  |  |  |  | 0.90528 | 25.1847

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent | pf_loading
0 | [14 empty] | 42.4334
1 | [14 empty] | 1.4085
2 | [14 empty] | 15.777
3 | [14 empty] | 15.8385
4 | [14 empty] | 26.08
5 | [14 empty] | 13.7748
6 | [14 empty] | 39.3604
7 | [14 empty] | 7.0831
8 | [14 empty] | 19.0017
9 | [14 empty] | 15.815
10 | [14 empty] | 15.8057
11 | [14 empty] | 19.0017
12 | [14 empty] | 66.1273
13 | [14 empty] | 9.7407
14 | [14 empty] | 5.6511
15 | [14 empty] | 37.8346
16 | [14 empty] | 15.7697
17 | [14 empty] | 22.0649

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent | pf_loading
0 | [13 empty] | 73.6058
1 | [13 empty] | 122.5602
2 | [13 empty] | 122.2327
3 | [13 empty] | 122.6163
4 | [13 empty] | 123.0932
5 | [13 empty] | 122.9114
6 | [13 empty] | 122.8393
7 | [13 empty] | 131.6477
8 | [13 empty] | 107.0789
9 | [13 empty] | 109.8781

## res_ext_grid
| p_mw | q_mvar | pf_p | pf_q
0 |  |  | -9.6158 | 11.1467

## res_sgen
| p_mw | q_mvar | pf_p | pf_q
0 |  |  | 0.9999 | -0.48427
1 |  |  | 5.363 | -2.5974
2 |  |  | 0.9999 | -0.48427
3 |  |  | 0.39996 | -0.19371
4 |  |  | 0.8698 | -0.42126
5 |  |  | 1 | -0.48432
6 |  |  | 1 | -0.48432
7 |  |  | 0.3597 | -0.17421
8 |  |  | 0.9999 | -0.48427

## res_switch
| i_ka | loading_percent | pf_closed | pf_in_service
0 |  |  | TRUE | TRUE
1 |  |  | TRUE | TRUE

## user_pf_options
max_iteration
0 | 10

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | description | object
6 | bus | substat | object
7 | bus | folder_id | object
8 | bus | sernum | object
9 | bus | for_name | object
10 | bus | chr_name | object
11 | sgen | name | object
12 | sgen | bus | int64
13 | sgen | p_mw | float64
14 | sgen | q_mvar | float64
15 | sgen | sn_mva | float64
16 | sgen | scaling | float64
17 | sgen | in_service | bool
18 | sgen | type | object
19 | sgen | current_source | bool
20 | sgen | description | object
21 | sgen | sernum | object
22 | sgen | for_name | object
23 | sgen | chr_name | object
24 | switch | bus | int64
25 | switch | element | int64
26 | switch | et | object
27 | switch | type | object
28 | switch | closed | bool
29 | switch | name | object
30 | switch | z_ohm | float64
31 | switch | in_ka | float64
32 | ext_grid | name | object
33 | ext_grid | bus | uint32
34 | ext_grid | vm_pu | float64
35 | ext_grid | va_degree | float64
36 | ext_grid | slack_weight | float64
37 | ext_grid | in_service | bool
38 | ext_grid | s_sc_max_mva | float64
39 | ext_grid | s_sc_min_mva | float64
40 | ext_grid | rx_min | float64
41 | ext_grid | rx_max | float64
42 | ext_grid | r0x0_max | float64
43 | ext_grid | x0x_max | float64
44 | ext_grid | r0x0_min | float64
45 | ext_grid | x0x_min | float64
46 | ext_grid | description | object
47 | line | name | object
48 | line | std_type | object
49 | line | from_bus | uint32
50 | line | to_bus | uint32
51 | line | length_km | float64
52 | line | r_ohm_per_km | float64
53 | line | x_ohm_per_km | float64
54 | line | c_nf_per_km | float64
55 | line | g_us_per_km | float64
56 | line | max_i_ka | float64
57 | line | df | float64
58 | line | parallel | uint32
59 | line | type | object
60 | line | in_service | bool
61 | line | r0_ohm_per_km | float64
62 | line | x0_ohm_per_km | float64
63 | line | c0_nf_per_km | float64
64 | line | alpha | float64
65 | line | temperature_degree_celsius | float64
66 | line | description | object
67 | line | line_idx | float64
68 | line | folder_id | object
69 | line | section_idx | int64
70 | trafo | name | object
71 | trafo | std_type | object
72 | trafo | hv_bus | uint32
73 | trafo | lv_bus | uint32
74 | trafo | sn_mva | float64
75 | trafo | vn_hv_kv | float64
76 | trafo | vn_lv_kv | float64
77 | trafo | vk_percent | float64
78 | trafo | vkr_percent | float64
79 | trafo | pfe_kw | float64
80 | trafo | i0_percent | float64
81 | trafo | shift_degree | float64
82 | trafo | tap_side | object
83 | trafo | tap_neutral | float64
84 | trafo | tap_min | float64
85 | trafo | tap_max | float64
86 | trafo | tap_step_percent | float64
87 | trafo | tap_step_degree | float64
88 | trafo | tap_pos | int32
89 | trafo | tap_phase_shifter | bool
90 | trafo | parallel | uint32
91 | trafo | df | float64
92 | trafo | in_service | bool
93 | trafo | vk0_percent | float64
94 | trafo | vkr0_percent | float64
95 | trafo | mag0_percent | float64
96 | trafo | mag0_rx | float64
97 | trafo | si0_hv_partial | float64
98 | trafo | tap_set_vm_pu | float64
99 | trafo | description | object
100 | trafo | equipment | object
101 | res_bus | vm_pu | float64
102 | res_bus | va_degree | float64
103 | res_bus | p_mw | float64
104 | res_bus | q_mvar | float64
105 | res_bus | pf_vm_pu | float64
106 | res_bus | pf_va_degree | float64
107 | res_line | p_from_mw | float64
108 | res_line | q_from_mvar | float64
109 | res_line | p_to_mw | float64
110 | res_line | q_to_mvar | float64
111 | res_line | pl_mw | float64
112 | res_line | ql_mvar | float64
113 | res_line | i_from_ka | float64
114 | res_line | i_to_ka | float64
115 | res_line | i_ka | float64
116 | res_line | vm_from_pu | float64
117 | res_line | va_from_degree | float64
118 | res_line | vm_to_pu | float64
119 | res_line | va_to_degree | float64
120 | res_line | loading_percent | float64
121 | res_line | pf_loading | float64
122 | res_trafo | p_hv_mw | float64
123 | res_trafo | q_hv_mvar | float64
124 | res_trafo | p_lv_mw | float64
125 | res_trafo | q_lv_mvar | float64
126 | res_trafo | pl_mw | float64
127 | res_trafo | ql_mvar | float64
128 | res_trafo | i_hv_ka | float64
129 | res_trafo | i_lv_ka | float64
130 | res_trafo | vm_hv_pu | float64
131 | res_trafo | va_hv_degree | float64
132 | res_trafo | vm_lv_pu | float64
133 | res_trafo | va_lv_degree | float64
134 | res_trafo | loading_percent | float64
135 | res_trafo | pf_loading | float64
136 | res_ext_grid | p_mw | float64
137 | res_ext_grid | q_mvar | float64
138 | res_ext_grid | pf_p | float64
139 | res_ext_grid | pf_q | float64
140 | res_sgen | p_mw | float64
141 | res_sgen | q_mvar | float64
142 | res_sgen | pf_p | float64
143 | res_sgen | pf_q | float64
144 | res_switch | i_ka | float64
145 | res_switch | loading_percent | float64
146 | res_switch | pf_closed | object
147 | res_switch | pf_in_service | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva | pf_converged
0 | 2.13.1 | 2.12.0 | FALSE | FALSE | Summary Grid | 50 | 100 | TRUE